AIG Programs

Loss Control Bulletin

Equipment Maintenance Checklist

Safety

Equipment should only be inspected, tested and maintained by qualified trained personnel. This document is meant as a guide to what actions should take place; it is not an instruction on how to complete the activities.

Operation

Continued safe operation of your equipment depends on regular maintenance and testing of its operating and protective controls. The tests outlined below are designed to determine whether or not the equipment and controls are in good operating condition. The applicable log sheet should be used to guide you and document results.

Repairs

Should any test indicate that the device being tested or observed is not in good operating condition, it should be repaired immediately. Record and maintain records of repairs or changes so that a complete record will be available for review at any time.

Records

Equipment procedures and maintenance guidelines should be kept in a central location for quick reference when needed. If missing, research manufacturers’ websites for the service, operating and parts manuals for the installed equipment models.

Instructions

Read and follow all manufacturers’ guidelines and instructions for periodic service, maintenance and inspection of equipment and systems.

Prepare!

You should have an emergency shutdown procedure for critical equipment. Educate key employees on how to implement these procedures.

Don’t wait for equipment failure!

Equipment Maintenance Checklist

Equipment/System

| BOILERS | Steam heating |
| --- | --- |
|  | high pressure |
|  | Over - 15psi |
|  | Caution – All |
|  | steam and water |
|  | discharges must |
|  | be piped to a |
|  | safe place. |

Steam

heating low

pressure15psi

and under

Caution – All steam and water discharges must be piped to a safe place.

Hot water heating160ºF & 250psi or less

Caution – All water discharge must be piped to a safe place.

|  |  |  |  |  |  |  | Reference |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | What to look for/What to do | Daily | Weekly | Monthly | Quarterly | Annually | document |
|  |  |  |  |  |  |  | # |
|  | Pump and system – Check feedwater and |  |  |  |  |  | 421 |
|  | condensate pumps for proper operation and leaky | • |  |  |  |  | 422 |
|  | packing. Examine traps, check valves, makeup float |  |  |  |  |  |  |
|  |  |  |  |  |  |  | 441 |
|  | valves, expansion or condensate tank, and other |  |  |  |  |  |  |
|  | parts of the system. |  |  |  |  |  |  |
|  | Low-water fuel cut-off – Drain float chamber while | • |  |  |  |  |  |
|  | boiler is running. This should interrupt the circuit and |  |  |  |  |  |  |
|  | stop the burner. |  |  |  |  |  |  |
|  | Burner operation – If the burner starts with a puff or | • |  |  |  |  |  |
|  | operates roughly, call your service personnel at once! |  |  |  |  |  |  |
|  | Safety/relief valve – Pull try-lever to full open |  |  |  |  |  |  |
|  | position with pressure on the boiler. Release try- |  | • |  |  |  |  |
|  | lever to allow the valve to snap closed. |  |  |  |  |  |  |
|  | Water column or gauge glass – Open the drain |  |  |  |  |  |  |
|  | valve quickly to void a small quantity of water. | • |  |  |  |  |  |
|  | Water level should return quickly when the drain |  |  |  |  |  |  |
|  | valve is closed. |  |  |  |  |  |  |
|  | Pump and system – Check feedwater and |  |  |  |  |  | 401 |
|  | condensate pumps for proper operation and leaky | • |  |  |  |  | 423 |
|  | packing. Examine traps, check valves, makeup float |  |  |  |  |  |  |
|  |  |  |  |  |  |  | 422 |
|  | valves, expansion or condensate tank, and other |  |  |  |  |  |  |
|  | parts of the system. |  |  |  |  |  |  |
|  | Low-water fuel cut-off – Drain float chamber while |  | • |  |  |  |  |
|  | boiler is running. This should interrupt the circuit and |  |  |  |  |  |  |
|  | stop the burner. |  |  |  |  |  |  |
|  | Burner operation – If the burner starts with a puff or | • |  |  |  |  |  |
|  | operates roughly, call your service personnel at once! |  |  |  |  |  |  |
|  | Safety/relief valve – Pull try-lever to full open |  | • |  |  |  |  |
|  | position with pressure on the boiler. Release try- |  |  |  |  |  |  |
|  | lever to allow the valve to snap closed. |  |  |  |  |  |  |
|  | Water column or gauge glass – Open the drain |  |  |  |  |  |  |
|  | valve quickly to void a small quantity of water. |  |  | • |  |  |  |
|  | Water level should return quickly when the drain |  |  |  |  |  |  |
|  | valve is closed. |  |  |  |  |  |  |
|  | Pump and system – Check feedwater pump for |  |  |  |  |  | 401 |
|  | proper operation and leaky packing. Examine | • |  |  |  |  | 423 |
|  | check valves, makeup float valves, expansion, and |  |  |  |  |  |  |
|  |  |  |  |  |  |  | 442 |
|  | other parts of the system. |  |  |  |  |  |  |
|  | Low-water fuel cut-off (If applicable) – Drain float |  |  |  |  |  |  |
|  | chamber while boiler is running. This should interrupt |  |  | • |  |  |  |
|  | the circuit and stop the burner. |  |  |  |  |  |  |
|  | Burner operation – If the burner starts with a puff or | • |  |  |  |  |  |
|  | operates roughly, call your service personnel at once! |  |  |  |  |  |  |
|  | Safety/relief valve – Pull try-lever to full open |  |  | • |  |  |  |
|  | position with pressure on the boiler. Release try- |  |  |  |  |  |  |
|  | lever to allow the valve to snap closed. |  |  |  |  |  |  |

Equipment Maintenance Checklist

Equipment/System

| AIR | Hermetic |
| --- | --- |
|  | Caution |
| CONDITIONING |  |
|  | cleaning or |
|  | - Always |
|  | de-energize |
|  | electrical |
|  | equipment |
|  | before testing, |
| & | performing |
| REFRIGERATION | maintenance. |

Non-hermetic Caution

– Always deenergize electrical equipment before testing, cleaning or performing maintenance.

|  |  |  |  |  |  | Reference |
| --- | --- | --- | --- | --- | --- | --- |
| What to look for/What to do | Daily | Weekly | Monthly | Quarterly | Annually | document |
|  |  |  |  |  |  | # |
| Motors – Take insulation resistance readings of motor |  |  |  |  |  | 406 |
| windings. If less than one megohm DO NOT start |  |  |  |  | • | 407 |
| motor. Check for the cause of Low Resistance. Note: |  |  |  |  |  |  |
|  |  |  |  |  |  | 425 |
| Hermetic motor readings less than 30 megohms |  |  |  |  |  |  |
| should be checked by a service technician. |  |  |  |  |  | 445 |
| Motor controls – Inspect starter contacts for |  |  |  |  |  | 448 |
| deterioration, pitting, corrosion, etc.; check |  |  |  |  |  |  |
| terminal connections for tightness; examine |  |  |  |  | • |  |
| overload protection for adequate size and defects; |  |  |  |  |  |  |
| determine that timing devices have correct operating |  |  |  |  |  |  |
| sequence; check mechanical linkage for binding |  |  |  |  |  |  |
| and looseness. |  |  |  |  |  |  |
| Fans – Check for broken, cracked, bent or loose |  |  |  |  |  |  |
| blades or hubs; check shaft and bearings; check belt |  |  |  |  | • |  |
| tension and condition. |  |  |  |  |  |  |
| Filters – Clean air filters serving the evaporator | • |  |  |  |  |  |
| and the air-cooled condenser. If a water-cooled |  |  |  |  |  |  |
| condenser is used, the water side must be kept clean. |  |  |  |  |  |  |
| Motors – Take insulation resistance readings of |  |  |  |  |  | 406 |
| motor windings. If less than one megohm DO NOT |  |  |  |  |  | 407 |
| start motor. Check for the cause of low resistance. |  |  |  |  | • |  |
|  |  |  |  |  |  | 425 |
| Check air ventilation openings on open-type motors |  |  |  |  |  |  |
| for obstruction. Check bearings on open-type |  |  |  |  |  | 445 |
| motors for adequate and proper lubrication. |  |  |  |  |  |  |
|  |  |  |  |  |  | 448 |
| Motor controls – Inspect starter contacts for |  |  |  |  |  |  |
| deterioration, pitting, corrosion, etc.; check |  |  |  |  |  |  |
| terminal connections for tightness; examine |  |  |  |  | • |  |
| overload protection for adequate size and defects; |  |  |  |  |  |  |
| determine that timing devices have correct operating |  |  |  |  |  |  |
| sequence; check mechanical linkage for binding |  |  |  |  |  |  |
| and looseness. |  |  |  |  |  |  |
| Fans – Check for broken, cracked, bent or loose |  |  |  |  | • |  |
| blades or hubs; check shaft and bearings; check belt |  |  |  |  |  |  |
| tension and condition. |  |  |  |  |  |  |
| Filters – Clean air filters serving the evaporator |  |  |  |  |  |  |
| and the air-cooled condenser. If a water-cooled |  | • |  |  |  |  |
| condenser is used, the water side must be kept clean. |  |  |  |  |  |  |
| Moisture indicator – Observe to determine any |  |  |  |  |  |  |
| change in the indicator chemical color or the |  | • |  |  |  |  |
| presence of gas bubbles in the liquid refrigerant. In |  |  |  |  |  |  |
| either case your service technician should be called. |  |  |  |  |  |  |
| Oil sight glass – Observe the glass to establish |  |  |  |  |  |  |
| that sufficient oil is in the compressor crankcase. |  | • |  |  |  |  |
| Oil leakage should not be tolerated. Any change |  |  |  |  |  |  |
| in normal oil level should be investigated by your |  |  |  |  |  |  |
| service technician. |  |  |  |  |  |  |
| Temperature – In-operation temperature levels for |  |  |  |  |  |  |
| the compressor suction and discharge should be |  |  |  |  |  |  |
| established and recorded. Any unusual change in |  | • |  |  |  |  |
| these temperatures should be called to the attention |  |  |  |  |  |  |
| of your service technician. |  |  |  |  |  |  |
| Pressure – Operating pressure levels should be |  |  |  |  |  |  |
| established and recorded. Any unusual change in |  | • |  |  |  |  |
| these pressures should be called to the attention of |  |  |  |  |  |  |
| your service technician. |  |  |  |  |  |  |

Equipment Maintenance Checklist

|  |  |  |  |  |  |  |  | Reference |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Equipment/System |  | What to look for/What to do | Daily | Weekly | Monthly | Quarterly | Annually | document |
|  |  |  |  |  |  |  |  | # |
| ELECTRICAL | Electrical | Cool – All vent and air circulation openings must be |  |  |  |  |  | 420 |
|  | - Always | Clean – Dust and/or dirt accumulations should be |  |  |  |  |  | 447 |
|  | distribution | clear and operational. Electrical loads should be |  |  | • |  |  | 443 |
|  | system | reviewed and corrected to ensure that circuits are |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | 446 |
|  | Caution | properly loaded and balanced. |  |  |  |  |  |  |
| / | deenergize | removed from the equipment and surroundings. |  |  |  |  |  |  |
| ELECTRONIC |  |  |  |  |  |  |  |  |
|  | performing | Equipment should be thoroughly cleaned inside |  |  |  |  |  |  |
|  | electrical |  |  |  |  |  | • |  |
|  | equipment | and outside. Space in switchrooms and switchgear |  |  |  |  |  |  |
|  | before testing, | enclosures should not be used for storing tools, |  |  |  |  |  |  |
|  | cleaning or | supplies, or other material. |  |  |  |  |  |  |
|  | maintenance. | Dry – Precaution should be taken to prevent steam, |  |  |  |  |  |  |
|  |  | chemicals, moisture, or condensation from entering |  |  | • |  |  |  |
|  |  | electrical enclosures. |  |  |  |  |  |  |
|  |  | Tight – Clean and tighten all loose parts and replace |  |  |  |  |  |  |
|  |  | any that war worn. Equipment should be manually |  |  |  |  | • |  |
|  |  | exercised to establish that moving parts do not bind |  |  |  |  |  |  |
|  |  | and are free to operate. |  |  |  |  |  |  |
|  | Electronic | Protection – Computers, associated components of |  |  |  |  |  | 420 |
|  | & computer | the computer system, and other electronic equipment |  |  |  |  |  | 443 |
|  | equipment | should be protected by a UL-listed surge suppression |  |  |  |  |  |  |
|  | Caution | device. Verify that vital programs and records are |  |  | • |  |  |  |
|  |  | stored remotely and/or in an approved safe located |  |  |  |  |  |  |
|  | – Always |  |  |  |  |  |  |  |
|  |  | in a low-hazard area, and protected by smoke |  |  |  |  |  |  |
|  | deenergize |  |  |  |  |  |  |  |
|  |  | detection and automatic sprinklers. |  |  |  |  |  |  |
|  | electrical |  |  |  |  |  |  |  |
|  | equipment | Heat – All vent and air circulation openings must be |  |  | • |  |  |  |
|  | before testing, | free from obstruction. Filters should be kept clean |  |  |  |  |  |  |
|  | cleaning or | and sound, and the fans operable. |  |  |  |  |  |  |
|  | performing | Smoke – Ensure that approved detectors are |  |  |  |  |  |  |
|  | maintenance. |  |  |  |  |  |  |  |
|  |  | installed and maintained. Verify that the actuation |  |  |  |  |  |  |
|  |  | of any detector results in the sounding of alarms and |  |  |  | • |  |  |
|  |  | the shut down of air conditioning equipment. |  |  |  |  |  |  |
|  |  | Dry – Precaution should be taken to prevent steam, |  |  | • |  |  |  |
|  |  | chemicals, moisture, or condensation from entering |  |  |  |  |  |  |
|  |  | computers or associated equipment. |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | Reference |
| Equipment/System |  | What to look for/What to do | Daily | Weekly | Monthly | Quarterly | Annually | document |
|  |  |  |  |  |  |  |  | # |
| MECHANICAL | Fans, blowers | Fans & blowers – Check for broken, cracked, bent |  |  |  |  | • | 420 |
|  | & air induction | or loose blades or hubs; check shaft and bearings; |  |  |  |  |  | 443 |
|  | louvers | check belt tension and condition. |  |  |  |  |  |  |
|  |  | Vents & louvers – Inspect for damage and |  |  |  |  |  |  |
|  |  | operation. Parts should be free of obstructions or |  |  |  |  |  |  |
|  |  | blockage that would prevent proper intake for |  |  | • |  |  |  |
|  |  | combustion air. Vents must not be blocked open; this |  |  |  |  |  |  |
|  |  | may cause excessive cold air induction and possible |  |  |  |  |  |  |
|  |  | freezing of vital systems. |  |  |  |  |  |  |
|  | Deepwell | Motors – Take insulation resistance readings of |  |  |  |  |  | 425 |
|  | pumps | motor windings. If less than one megohm DO NOT |  |  |  |  |  |  |
|  |  | start motor. Check for the cause of low resistance. |  |  |  |  | • |  |
|  |  | Check air ventilation opening on open-type motors |  |  |  |  |  |  |
|  |  | for obstruction. Check bearings on open-type |  |  |  |  |  |  |
|  |  | motors for adequate and proper lubrication. |  |  |  |  |  |  |
|  |  | Motor controls – Inspect starter contacts for |  |  |  |  |  |  |
|  |  | deterioration, pitting, corrosion, etc.; check terminal |  |  |  |  | • |  |
|  |  | connections for tightness; examine overload |  |  |  |  |  |  |
|  |  | protection for adequate size and defects; check |  |  |  |  |  |  |
|  |  | mechanical linkage for binding and looseness. |  |  |  |  |  |  |

Equipment Maintenance Checklist

|  |  |  |  |  |  |  |  | Reference |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Equipment/System | What to look for/What to do | Daily | Weekly | Monthly | Quarterly | Annually | document |
|  |  |  |  |  |  |  |  | # |
| MISC | Hot water heaters | Relief valve – Pull try-lever to full open |  |  | • |  |  | 423 |
|  |  | position with pressure on the equipment. |  |  |  |  |  |  |
|  |  | Release try-lever to allow the valve to snap |  |  |  |  |  |  |
|  |  | closed. Caution – All discharges must be |  |  |  |  |  |  |
|  |  | piped to a safe place. |  |  |  |  |  |  |
|  | Food preparation | See “Commercial Cooking Equipment |  |  |  |  |  | 438 |
|  | equipment, pressurized | Cleaning & Maintenance procedures” |  |  |  |  |  |  |
|  | cookers, steam kettles & | wallchart. |  |  |  |  |  |  |
|  | appliances |  |  |  |  |  |  |  |
|  |  |  | National toll-free inspection hotline |  |  |  |  |  |
|  | Reference documents via www.HSB.com |  | Inspection questions, requests for |  |  | Telephone: 800-333-4677 |  |  |
|  | Reference documents for all of the above checklist items are available |  | reference documents or status of |  |  | Fax: 800-292-4083 |  |  |
|  |  |  | scheduled inspections can be made |  |  |  |  |  |
|  | through HSB.com. |  |  |  |  | E-mail: NSCINSP_hotline@hsb.com |  |  |
|  |  |  | directly to HSB’s national |  |  |  |  |  |
|  |  |  | Inspection Hotline. |  |  |  |  |  |

Keep A Record of Your Service Contractors for Quick Reference

| Service Contractor | Company | Name | Telephone | Fax |
| --- | --- | --- | --- | --- |
| Heating |  |  |  |  |

Cooling And Refrigeration

Electrical

Plumbing

Utility

Other

Contact:

AIG Programs Loss Control

T 800 611 3994

F 888 659 9047

programslc@aig.com

© 2014 The Hartford Steam Boiler Inspection and Insurance Company. All rights reserved.  #433 (rev 07/14). Used with permission of The Hartford Steam Boiler Inspection and Insurance Company.

The services described herein are intended for the express purpose of assisting AIG underwriting personnel in the underwriting of the subject insured’s risk exposures, property and/or operations and to assist in loss control activities. No warranty, guarantee, or representation, either expressed or implied, is made as to the correctness or sufficiency of any such service. Services may not address each and every possible loss potential, violation of any laws, rules or regulations, or exception to good practices and procedures. AIG assumes no responsibility for the discovery and elimination of hazards which could possibly cause accidents or damage at any facility that is inspected. Reliance upon, or compliance with, any of the information, suggestions or recommendations contained in any of the services described herein in no way guarantees the fulfillment of any insured’s obligations under its insurance policy or as may otherwise be required by any laws, rules or regulations

American International Group, Inc. (AIG) is a leading international insurance organization serving customers in more than 100 countries and jurisdictions. AIG companies serve commercial, institutional, and individual customers through one of the most extensive worldwide property-casualty networks of any insurer. In addition, AIG companies are leading providers of life insurance and retirement services in the United States. AIG common stock is listed on the New York Stock Exchange and the Tokyo Stock Exchange.

Additional information about AIG can be found at www.aig.com | YouTube: www.youtube.com/aig | Twitter: @AIGinsurance | LinkedIn: www.linkedin.com/company/aig

AIG is the marketing name for the worldwide property-casualty, life and retirement, and general insurance operations of American International Group, Inc. For additional information, please visit our website at www.aig.com. All products and services are written or provided by subsidiaries or affiliates of American International Group, Inc. Products or services may not be available in all countries, and coverage is subject to actual policy language. Non-insurance products and services may be provided by independent third parties. Certain property-casualty coverages may be provided by a surplus lines insurer. Surplus lines insurers do not generally participate in state guaranty funds, and insureds are therefore not protected by such funds.

© American International Group, Inc. All rights reserved.	10/15 SP540T