Town of Bar Harbor

Planning & Code Enforcement

Vacation Rental Inspections Checklist

All vacation rentals shall comply with chapters 4 “General”, 6 “Classification of Occupancy”, 7 “Means of Egress”, 9 “Building Service and Fire Protection Equipment”, 24 “One-and Two-Family Dwellings”, 30 “New Apartment Buildings” and 31 “Existing Apartment Buildings” of the 2018 NFPA 101 Life Safety Code, as most recently amended and edited, and as applicable.

Property Address: ___________________________	Map and Lot: _______________

Name of Property Owner(s): ______________________________________________

Mailing Address: _______________________________________________________

Telephone Number(s) of Owners: __________________________________________

Property Contact Name:  ______________________	Email: ____________________

Smoke Detection 24.3.4.1.1

Are there HARD WIRED, INTERCONNECTED smoke detectors located:

| ____ | On every level of the dwelling |  |  |  |
| --- | --- | --- | --- | --- |
| ____ | In the basement |  |  |  |
| ____ | In every bedroom |  |  |  |
| ____ | Outside of each sleeping area, in the immediate vicinity of the sleeping rooms |  |  |  |
| ____ | In high hazard areas such as boiler rooms, laundry rooms, and attached garage |  |  |  |
| Carbon Monoxide Detection 24.3.4.2 |  |  |  |  |
| ____ | Installed in the area within the bedroom(s) or giving access to the bedroom(s) |  |  |  |
| ____ | On every level of the dwelling unit, including basements |  |  |  |
| Electrical – 2017 National Electrical Code |  |  |  |  |
| ____ | Are all the receptacles properly grounded and functioning? |  |  |  |
| ____ | Are all the panels clearly marked? |  |  |  |
| ____ | Are there ground fault circuit interrupter receptacles located in: |  |  |  |
|  | ____ |  | in the bathrooms |  |
|  | ____ |  | in the kitchens |  |
|  | ____ |  | in the garage |  |
|  | ____ |  | in the basement |  |
|  | ____ |  | around the exterior of the building? |  |
| ____ | Is there any unnecessary use of extension cords? |  |  |  |
| ____ | Is all wiring secured with staples or running boards? |  |  |  |

Fire Extinguisher – Is there a fire extinguisher:

| ____ | Mounted and visible to tenants? |  |  |  |
| --- | --- | --- | --- | --- |
| Egress |  |  |  |  |
| ____ | Do all rooms of occupancy meet the ceiling height requirement of 7’-6” for at |  |  |  |
|  | least two thirds of the rooms’ size? (Section 7.1.5) |  |  |  |
| ____ | Do all egress doors have a clear width of 32” to facilitate egress? (Section |  |  |  |
|  | 7.2.1.2.3) |  |  |  |
| ____ | Are all floors level with minimum changes in elevation? (Section 7.1.6.2) |  |  |  |
| ____ | Are all hallways at least 36” wide with minimum projections entering the space, |  |  |  |
|  | including furniture and decorations? (Section 24.2.6) |  |  |  |
| ____ | Are all stairs uniform in tread space and riser height? (Section 7.2.2) |  |  |  |
| ____ | Are all locks on the doors in the egress passages easily unlocked without any |  |  |  |
|  | undue hardship or tools? (Section 24.2.2.3.3) |  |  |  |
| ____ | Do the one and two-family dwellings have a primary and secondary means of |  |  |  |
|  | egress? (Section 4.5.3.1) |  |  |  |
| ____ | Every bedroom shall have a window or door leading to the exterior with a clear |  |  |  |
|  | opening of not less than 5.7 square feet, and with a width of not less than 20”, |  |  |  |
|  | and a height of not less than 24”. The bottom of the opening shall be not more |  |  |  |
|  | than 44” above the floor. (Section 24.2.2.3.3) |  |  |  |
| ____ | No sleeping rooms or living areas shall be accessible only by a ladder, a stair |  |  |  |
|  | ladder, an alternating tread device or folding stairs. (Section 24.2.5.6) |  |  |  |
| ____ | Are there any third-floor bedrooms? |  |  |  |
|  | ____ |  | Do they have fire escape stairs? |  |
| ____ | Is there an attached garage? |  |  |  |
|  | ____ |  | is it completely enclosed with fire grade sheetrock? |  |
|  | ____ |  | is there a fire door leading into the structure? |  |
| General Housekeeping |  |  |  |  |
| ____ | Are critical areas free of combustible materials and obstructions? |  |  |  |
| ____ | Are the exit passages free of obstructions including furniture, bikes, decorations, |  |  |  |
|  | etc? |  |  |  |
| ____ | Has the renter been provided with important information such as contact |  |  |  |
|  | telephone numbers? |  |  |  |
| ____ | Does the renter have clear directions to the property? |  |  |  |
| ____ | Is there appropriate signage with the approved E-911 address clearly visible? |  |  |  |

Page 2 of 4	12/04/20

Heat Sources

| ____ | Has the heating unit been tagged with a minimum annual service test and |  |
| --- | --- | --- |
|  | cleaning conducted by a licensed technician? |  |
| ____ Oil-Fired Unit |  |  |
|  | ____ | Does the unit have primary and secondary safety controls? |
|  | ____ | Is there a red emergency shut off switch located outside the area? |
|  | ____ | Is there a technician shut off switch located at the burner? |
|  | ____ | Is there a thermal coupling switch located over the heating unit? |
|  | ____ | Is there a low water cutoff located on the water-based unit? |
|  | ____ | Is the chimney connector sound and properly connected? |
|  | ____ | Is the unit placed on non-combustible flooring as required? |
|  | ____ | Is the oil-line protected from injury by non-metallic sheathing? |
|  | ____ | Is there a shut-off valve at the tank and beyond the filter for routing |
|  |  | servicing for the filter? |
|  | ____ | Is the oil tank properly supported on cement flooring or a pad with legs no |
|  |  | more than 12” off the floor and with flanged supports on each leg base? |
|  | ____ | Is the tank liquid tight? |
|  | ____ | Are the fill and vent tank connectors properly sized? |
|  | ____ | Is there a Power Venter? |
| ____ | Propane Unit |  |
|  | ____ | Is the tank supported on a firm cement footing or level pad? |
|  | ____ | Is there appropriate fuel piping from the tank to the appliance? |
|  | ____ | If the appliance is listed for gas service, is the listing label visible on the |
|  |  | unit with clearance to all combustibles per the listing of the unit? |
|  | ____ | Is the emergency shut off switch installed and clearly marked? |
|  | ____ | Is the blue emergency shut-off valve located within 6-feet? |
|  | ____ | Is there appropriate flue gas venting of the appliance? |
|  | ____ | Are propane gases vented to the same flue as a solid fuel burning device? |
|  | ____ | Are all direct venting appliances properly vented to the outside with |
|  |  | relation to ground level and proper distances maintained from windows, |
|  |  | doors, and mechanical devices which draw air into the building? |
|  | ____ | Are all primary safety controls installed per the product listing? |

Page 3 of 4	12/04/20

____	Solid Fuel Burning Device

____	Will the renter be using the device?  If not, is the device clearly marked not

to use?

____	Is the appliance listed for solid fuel use?

____	Is there appropriate floor protection under the unit?

____	Is the proper chimney vent connector installed?

____	Does the unit have the appropriate clearance from combustibles?

____	are there appropriate heat shields as required?

____	Is the unit free from rust and corrosion?

____	Is the appliance properly connected to the appropriate chimney?

____	Is there proper clearance around the chimney for combustibles?

____	Has the chimney been cleaned as needed or on an annual basis?

Date of Inspection: ______________	Pass □	Fail □

Inspector Name: _________________________________________________

Inspector Signature: ______________________________________________

NOTES:

______________________________________________________________________

______________________________________________________________________

______________________________________________________________________

______________________________________________________________________

______________________________________________________________________

______________________________________________________________________

______________________________________________________________________

______________________________________________________________________

Fire Chief Signature: _____________________________	Date: ___________

Page 4 of 4	12/04/20